## Bill of Quantities
ITEMS | DESCRIPTION
1 | Preliminaries I
1.1 | Provide allowance for mobilization of all necessary labor, tool, emergency power supply & equipment and material, subsequently dismantle or remove from the site all temporary works, utilities, facilities, for this Works and for compliance to the Health, Safety and Environmental Requirements, and all of the Contractor's obligations under this Contract.
1.2 | Provide and maintain a weighing scale for the record of tare, gross and net weight for the sale of recyclable scrap material (including sorting by material classification if request)
1.3 | Provide the Insurances for third party and property, inclusive of CEM; as well as Labors, Material and Equipment as all the necessary coverage and required by Macau Law. Including the provision and demolishing license for the civil works.
1.4 | Prepare, submit and implement Environmental, Safety and Health Plan.
1.5 | Prepare and submit Environmental Impact Assessment Outline and Environmental Monitoring and Audit Outline Report
1.6 | Prepare and submit the EIA report, and Environmental Monitoring and Audit Report (prior project execution)
1.7 | Prepare and submit method statement for the Works.
1.8 | Provide the Comprehensive Risk Assessment Plan for Demolition Works.
1.9 | Prepare and submit Site Remediation Assessment Outline Report
1.1 | Final Site Remediation Assessment Outline Report shall be submitted Prior Phase 3 Execution (Decontamination)
1.11 | Prepare and submit Project completion report for each Phase including Final G01 – G04 DDD report
2 | Preliminaries II: SCR/Ammonia system & Asbestos survey & report, removal and disposal
2.1 | Conduct a comprehensive survey of asbestos-containing material (ACM) and provide an independent third-party laboratory report of the survey result for the whole project (including but not limited: From Item 3 to Item 28; Item 33; Item 39; Item 40 and HVAC System from Chemical Lab)
2.2 | Perform a thorough removal of all ACM from the plant before any dismantling work.
2.3 | Final disposal of the ACM in accordance with the relevant government laws and regulations.
2.4 | Conduct a comprehensive survey of the ammonia waste inside the SCR/Ammonia system and provide an independent third-party laboratory report of the survey result (including but not limited: Item 14.3, Item 16, Item 21 and Item 23)
2.5 | Perform a thorough removal of all SCR Ammonia Waste from the plant before any dismantling work.
2.6 | Final disposal of the SCR Ammonia Waste in accordance with the relevant government laws and regulations.
2.7 | The procedures must follow according to appendix
2.8 | From 2.1 to 2.7 must be done by qualified third party for survey & report, removal and disposal; and by qualified third party for quality control of every procedure.
3 | G01-G04 Heavy Fuel Oil Transfer Pump Station
3.1 | Removal of HFO Transfer pump A, B, C, filters and associated peripherals.
3.2 | Removal of HFO & steam tracing pipes to G01-G04 HFO Service Tank Farm.
3.3 | Removal of HFO Sludge transfer pump and associated peripherals.
4 | G01-G04 Cooling Water Pump & Chlorination Building
4.1 | Removal of all pumps, filtration system, chlorine dosing system and all associated peripherals, facilities, support frame and concrete plinths, pipes, overhead crane, roller gates and electrical & control system.
4.2 | Removal of underground pipes tot G03/G04, and from the buildings to sea water discharge at G01/G04 oil separator.
4.3 | To blank and remove compressed air and chlorine injection pipes.
4.4 | Demolition of CWP and Chlorination buildings down to road level, and backfill all basements, trenches and voids with demolition rubble to road level
4.5 | Backfill all pipe and cable trenches, and reinstatement of the surface areas.
5 | G01-G04 Chemical Effluent System
5.1 | Reroute the stainless steel effluent pipe from the Chemical Store to connect with G05/G08 chemical effluent pipe.
5.2 | To reconnect with the existing chemical effluent pipe inside the pipe trench and remove all decommissioned pipes.
5.3 | Removal of pumps and associated equipment of CP1 pit, demolition of concrete plinth and removal of decommissioned pipes.
6 | G01-G04 Sewerage System
6.1 | To backfill G01/G04 decommissioned sewerage network.
7 | Deactivate the Black Start function of G01-G04
7.1 | To disconnect and remove the power cables and other related connections as and to provide support to CEM during and after commissioning and tests of the Black Start system
7.2 | To isolate, disconnect and remove the interconnection MV cables between EGCB4 of HVS-11-EMG in G07/G08 HV Room and G4ECB of HVS-11-4 in G03/G04 HV Room
7.3 | To isolate, disconnect and remove the interconnection cables between EMGT-2 breaker in G07/G08 EMG Room and EMGT-3 breaker in G01/G02 LV Room, including transformers and other accessories
7.4 | To isolate, disconnect and remove all wirings from G05/G08 to JB-EMG as per the wiring list JB-EMG.
8 | G01/G02 Steam Turbine Generators & Auxiliaries and Building
8.1 | Removal of steam turbine generators and auxiliary facilities, associated peripherals, pipes, support structures, platforms, overhead crane and roller gates; electrical systems comprising of control consoles, panels, cabinets, switchgears, cables; any other building contents and facilities.
8.2 | Demolition of the building.
9 | G01/G02 Main & Auxiliary Transformers
9.1 | Decommissioning and removal of seven units of transformers.
9.2 | Removal of all cables from the Main transformers to the Substation and from Main transformers to the G01/G02 Steam Turbine
9.3 | Demolition of the transformer bays' walls and support bases.
10 | Decommissioning of G01/G02 Electrical and C&I Systems
10.1 | To dismantle and remove all decommissioned components.
11 | Decommissioning of G01/G02 Common Plant Auxiliaries
11.1 | To dismantle and remove all decommissioned components.
12 | G01/G02 Stack
12.1 | Removal of pipes, cables, support frame and concrete plinths. Demolition of the stack and site remediation.
13 | G01/G02 Decommissioning & Demolition Works
13.1 | Steam turbine and generators
13.2 | Station cooling and clean water systems
13.3 | Air Compressors
13.4 | 66/11kV transformers
13.5 | 11/3kV transformers
13.6 | 3/0.4kV transformers
13.7 | Equipment in Control Room
13.8 | Equipment in LV Room
13.9 | Equipment in MV Room
13.1 | Overhead crane
13.11 | Demolition of the building and site remediation
14 | G03/G04 Diesel Generators and Building
14.1 | Removal of the diesel engine generators, steam turbine generators and auxiliaries, all associated peripheral equipment, facilities, pipes, overhead crane and roller gates; electrical systems comprising of control consoles, panels, cabinets, switchgears, cables; any other building contents and facilities.
14.2 | Demolition of the building and connector with G01/G02 Building including concrete foundation, floors and sump pits up to the pile caps. All trenches, sump pits and voids to be backfilled and compacted with demolition rubble to level with the road.
14.3 | Removal of the two SCR systems.
14.4 | Decommissioning/removal of G03/G04 facilities
14.5 | Removal of the diesel oil pipe and supports from G03/G04 Diesel generator building to the terminal point at the G03/G04 DO transfer pump station. The terminal point shall be blanked with blind flange.
14.6 | Blanking of the terminal points at DO tank with blind flanges and remove the diesel oil pipes from DO storage tank to G03/G04 Fuel oil treatment building. To seal all wall penetrations.
14.7 | Blanking at the terminal points of the LO tanks and removal of the Main & Cylinder lube oil pipes from LO storage tanks to G03/G04 Diesel generator building including the LO pump station and all associated equipment, pipes, cables and supports. To seal all wall penetrations. Demolition of the pump containment bund and plinths to ground level.
14.8 | Demolition of the building.
15 | G03/G04 Main & Auxiliary Transformers
15.1 | Decommissioning and removal of eight units of transformers.
15.2 | Removal of all cables from the Main transformers to the Substation and from Main transformers to the G03/G04 Diesel building.
15.3 | Demolition of the transformer bays' walls, fencing and foundations.
16 | G03/G04 SCR Air Compressor Station
16.1 | Removal of air compressors, tanks and all associated equipment, pipes, cables, canopy and supports.
16.2 | Removal of all pipes, cables and supports from air receivers to G03/G04 Diesel building.
16.3 | Demolition of the plinths.
17 | G03/G04 ISO Storage Tank Farm
17.1 | Removal of tanks, transfer pumps and all associated equipment, pipes, cables and supports.
17.2 | Demolition of the bund wall and plinths.
18 | G03/G04 Fuel Oil Treatment Plant
18.1 | Removal of all equipment and other contents, demolition of the building.
18.2 | Removal of Fuel Oil Transfer Pump set and demolition of plinth.
19 | Decommissioning of G03/G04 Electrical and C&I Systems
19.1 | To dismantle and remove all decommissioned components.
20 | Decommissioning of G03/G04 Common Plant Auxiliaries
20.1 | To dismantle and remove all decommissioned components.
21 | G03/G04 Stack and Exhaust gas ducts
21.1 | Removal of G03 and G04 steel chimneys, all associated equipment, emission monitoring cubicle, supports and systems. Removal of exhaust gas ducts, supports and associated peripherals.
21.2 | Removal of G03/G04 stack
22 | G03/G04 Boiler Effluent Tanks
22.1 | Demolition of the plinths and site remediation.
Decommissioning & Modification of Common Auxiliary Systems
23 | Compressed Air System & G03/G04 Ammonia System Modification
23.1 | Decommission and blank the G03/G04 ammonia supply and return stainless steel pipes.
23.2 | To install stainless steel pipe and ball valve at the tie-in to G05/G06 SCR compressed air system to the existing ammonia supply pipe near G03/G04 Ammonia Supply Pump Station.
23.3 | To install a T-joint at tunnel entrance and stainless steel pipe to connect to existing control and service air pipes of the HFO storage tank with a new header; provide isolating valves and a filter/pressure regulator valve set. To install a ball valve at the T-joint and a new galvanized pipe to supply compressed air pipe to G05/G08 CWP building.
23.4 | To construct a new pipe trench to route the new pipe from tunnel entrance into the new pipe trench to connect with existing compressed air supply line for G05/G08 CWP building.
24 | SAAM Water Supply System
24.1 | To install a ball valve and a galvanized pipe from the main SAAM water supply line at the tunnel entrance and connect to existing water supply pipe to G05/G08 CWP building and remove decommissioined pipes.
24.2 | To install a new pipe from G05/G08 CWP to Guard House B.
24.3 | To plug and remove the SAAM water pipe to G01/G04 CWP building.
25 | Auxiliary Steam System
25.1 | To blank and remove decommissioned condensate pipes.
25.2 | To re-route a new steam pipe up the hillside to HFO tank farm.
25.3 | To install a new steam pipe to connect to the existing steam supply pipe for G01/G04 Oil Separator.
25.4 | Removal of all decommissioned steam pipes.
26 | Oily Water/Oily Sludge System
26.1 | Removal of Common sludge tank, K3 sludge oil transfer pump station, pipes, cables, supports and associated peripheral equipment; demolition of tank foundations and bund walls.
26.2 | Blank K3 Sludge oil transfer pipe at tunnel entrance and remove pipe to K3 Sludge oil transfer pump station.
26.3 | To reroute the waste oil transfer pipe from G01/G04 Oil Separator to CCA WWTP Oily sludge tank.
26.4 | To remove G01/G04 waste oil transfer pipe from G01/G04 Oil Separator to G01/G02 FO Tank Farm.
26.5 | To blank and remove G05/G08 sludge oil transfer pipe to Common Sludge Tank.
26.6 | Reinstatement of G05/G08 ISO tank farm and containment bund walls.
26.7 | To reinstate the insulation and stainless steel cladding on the designated ISO tank.
26.8 | Installation of the ISO tank unloading pump station.
26.9 | To supply and install a new steel pipe with insulation and cladding from G05/G08 common sludge oil header to designated ISO tank.
26.1 | Installation of the K3 sludge oil transfer pump station, including all associated valves and accessories; pipelines, heat tracing, insulation & cladding, grating platform and pump support.
26.11 | Installation of new pipe with an isolating ball valve from outlet pipe of G5-G08 Common sludge tank TA-FO-427 to K3 Sludge oil transfer pump station inlet pipe
26.12 | Installation of a new steel pipe from outlet of K3 Sludge oil transfer pump station to connect with the existing sludge oil transfer pipe to CCB K3 tank
26.13 | Installation of the G5-G8 Oil interceptor transfer pump.
26.14 | Re-route oily water drain pipes from HFO storage tank farm and HFO mixing pump station to G01/G04 oil separator.
26.15 | Re-route oily water pipe from K3 tank to G01-G04 Oil separator.
26.16 | Removal of OP1 equipment, oily wastewater and sludge pipelines and backfill trenches.
27 | WWTP modification
27.1 | Install steam heating inside Sludge Tank
27.2 | Install steam heating inside Oily Sludge Tank
27.3 | Change larger sludge pump No.1/2 (1101/1102) for more power to pump out the sludge to G12 sludge tanks and CCB K3 tank
28 | G01/G04 Interceptor Area and G05/G08 Interceptor Area
28.1 | Provide the design and execution for Raining Water Collection for G01/G04 Interceptor Area
28.2 | Cleaning/Refurbish G01- G04 HFO Interceptor Tank
28.3 | Cleaning/Refurbish G05- G08 HFO Interceptor Tank
28.4 | Site Modification
29 | Civil Construction
29.1 | Design, supply and install new air compressor for chemical lab office (including all pipelines and fittings)
29.2 | Design, supply and install new Demi water supply for chemical lab office (including all pipelines and fittings)
30 | G05/G08 Sea Water Intake Pumping House – Indoor Civil Recondition
30.1 | Provide the material and Indoor Civil Recondition
Relocation & Modification of Electrical, C&I and Network Systems Power Supply and Control for Plant Auxiliaries
31 | ISO Tank Farm electrical system installation
31.1 | To design and install the local control panels and the power supply for the pumps and panels, fed from DB4
31.2 | To provide the heat tracing element and other related equipment.
31.3 | To supply power for the heat tracing elements from the existing panels HT TF or HT FOT
Plant Extra-Low Voltage (ELV) System
32 | To supply and install an armored low voltage power cable from DB4 to the the local control box of relocated K3 Sludge oil transfer pump station
32.1 | To install an outdoor distribution board DB4 at K3 Sludge oil transfer pump station
32.2 | To supply and install the armored low voltage power cables from G07/08 BSS Cubicle 18C to DB4
32.3 | To provide and install 250A fuses switch in G07/08 BSS Cubicle 18C
33 | Demolished of the Oily Water/Waste Oil Treatment Facilities including power supply(OP1 and CP1)
33.2 | To dismantle the level sensor CP1, respective transmitter and junction box beside G02 Steam Boiler. The cable connection between the CP1 junction box and level instrument power supply panel/local PLC panel as mentioned Item 37.2 shall be disconnected, isolated and removed.
33.3 | To dismantle the local control panel in CCA Demi Plant Control Room, which remotely control OP03A, OP03B and OP03C oil pumps. The cables for the wiring connections between the control panel in CCA Demi Plant and the local control at the oil interception equipment platform shall be isolated, disconnected and removed.
33.4 | To isolate, disconnect and remove the control cables from the local oil content detection panel at the interception equipment platform to CCA Demi Plant Control Room.
33.5 | To disconnect and remove all decommissioned components and cables
34 | To design and install the local control panel and the 3-phase power supply cable for G05/G08 Oil interceptor transfer pump electrical system
35 | Public Announcement (PA) System
35.1 | The PA related to the demolished buildings required to be tested under the supervision of existing service. It is recommended to subcontract the current CPS CCTV cameras maintenance service contractor. The isolated PA must be returned to CEM.
36 | Plant Supervision System - Closed Circuit Television System (CCTV) and Access Control System Network (ACS)
36.1 | To relocate the existing network switch box CCA2 mounted on G01/04 Oil Treatment Building to CCA G05/G08 CWP building
36.2 | To supply and install new armored 12-core single mode fiber optics cable for connecting the network switch box CCA4 to the relocated CCA2 switch box.
36.3 | To supply and install new armored single mode 12-core optic fiber cable between CCA1 and switch box in new Gate House B
36.4 | To supply, and install CCTV cameras, including accessories, power supply, network switches for full coverage of the demolition area
36.5 | To reconnect the whole CCTV/ACS system complex to the modified CEM plant network
36.6 | Test and commissioning for ensuring the system integrity and functionality of the plant supervision system
36.7 | To supply, and install CCTV cameras, including accessories, power supply, network switches for new fence
37 | Street Lighting System
37.1 | To supply and install the armored LV cables and power supply from DB2 or DB3, with protection, for the street lights which are outside the demolition area and supplied by the lighting panel in G01/02 building, or LLDP-10 in existing PWT Control Room, and from Gate house B to G05-G08 chlorination station.
37.2 | To supply and install outdoor LED street lights, mounted on new lamp poles or on existing structures, at the CCA PWT Area side and for the "Access Road" routes
38 | Earthing and Lightning Protection System
38.1 | Retrofit the Existing Earthing System in G03/G04 Demolition areas
38.2 | To supply and install earth pits with earth electrodes
38.3 | To retrofit the existing earthing system for connecting the newly added earth pits and electrodes to the existing main earth grid, and also adding the earth conductors for connecting the specified existing earth pits
38.4 | To test and measure the earth resistance values of the new and existing earth electrodes
38.5 | Earthing System modification
39 | CCA Maintenance Building
39.1 | Removal of all equipment, pipes, crane, electrical systems and other contents.
39.2 | Demolition of the building and site remediation.
40 | CPS Oily Water & Storm Water Drainage System
40.2 | Cleaning of G05/G08 Common Sludge Storage Tank ;
40.3 | CCA HFO Tanks Farm drainage system modification.
41 | 3D Scanner
41.1 | To provide the 3D scan for all the facilities and building before demolition
42 | Fencing for Gate house B to G05-G08 chlorination station
42.1 | Provide design, material ans installation for the fencing from Gate house B to G05-G08 chlorination station
43 | CCA Domestic Waste Water System
43.1 | Provide the design, material and installation of CCA Domestic Waste Water System of CCA for ETS, CCA Warehouse, Chemical Lab, Chemical Store and Gate House B to be connected to the existing CCA Domestic Waste Water System.
44 | Decontamination
44.1 | Tank Farms, Engine Room and daily Tanks etc. G03/G04 ISO Storage Tank Farm Oily Water/Oily Sludge System G03/G04 Fuel Oil Treatment Plant G01-G04 Sludge Oil Tank Farm
45 | Demobilization
45.1 | Site clearance & reinstatement and demobilization after the completion of all Works.
46 | Supply and install electric heat tracing elements on a single designated ISO tank (maximum capacity of 21,000 liters) at the specified location, along with the reinstatement of insulation and stainless-steel cladding”, by installing heat tracing on three designated ISO tanks to enhance capacity.

## Recyclable Scrap Material
Item | Description of Scraps | UOM | Price in MOP
1 | Transformers變壓器 | Unit
2 | RMU環路開關 | Unit
3 | Exhaust valve housing | Piece
4 | Steel boiler tube | Ton
5 | Steel exhaust duct | Ton
6 | Cylinder liner | Unit
7 | SCR expansion joint | Unit
8 | Stationary machines | Unit
9 | Fuse, circuit breakers, miniature circuit breakers and current transformer | Ton
10 | Lead Seal | Ton
11 | Different Materials其他設備 | Ton
12 | Iron | Ton
13 | Aluminium Cables鋁心電纜 | Ton
14 | Copper cables銅心電纜 | Ton
15 | SMD ICs and Semiconductors | Ton
16 | Passive Components and Connectors | Ton
17 | Copper Wires and Wire Modules | Ton
18 | Electrical Scrap | Ton
Remark | The price should be following the marketing prices, the average will consider in every 3 months