TECHNICAL SPECIFICATION

For

Maintenance Service of Thermal Insulation for Coloane Power Station

TABLE OF CONTENTS

1.	PRELIMINARIES	4

1.1	Introduction	4

1.2	Scope of the Works	4

1.3	Description of the Works	4

1.4.	Site Inspection	5

1.4.1.	Location	5

1.4.2.	Site Visit	5

1.5.	Safety, Health and Environmental Precautions	6

1.6.	  CEM Green Compliance Requirement	7

1.7. Protection of the Properties	7

1.8.	Materials and Workmanship	7

1.8.1	Compliance with Regulation	7

1.8.2	Proprietary Articles	7

1.8.3.	Samples	7

1.8.4.	Safe Custody of Materials	8

1.8.5.	Loading and Unloading of Materials	8

1.9.	Program and Reports	8

1.10.	Temporary Works	9

1.10.1	Plant, Tools, Etc. and Scaffolding	9

1.10.2.	Contractor’s Storage Sheds, Workshops and Offices	9

1.10.3.	Water, Electrical Power and Compressed Air for the Works	9

1.10.4.	Other Temporary Works	10

1.11.	 Clearance of Site on Completion	10

1.12.	 Penalty	10

1.12.1.	Due to delays on the works	10

1.12.2.	Due to non compliance of CEM’s Safety and Environment requirements	11

1.13.	 Guarantee	11

1.14.	 Price	11

1.15.   General Remarks for this Specific Project	11

2.	SCHEDULE OF RATES	12

3.	CONTRACT EXECUTION	13

3.1.	 Description of the Works	13

3.2	 Time for Completion of the Work	13

3.3.	 Works Procedure	13

3.3.1.	Preparation	13

3.3.2.	Execution	13

3.3.3.	Other Contractor Responsibility	14

4.	APPENDIX 1	14

4.1.	Scope of works	14

4.2.	Insulation Material	14

4.3.	Metal Cladding Material	16

4.4.	Security Material	16

4.5.	Removal of Existing Insulation and Cladding	17

4.6.	Installation Specification	17

4.6.1.	General	17

4.6.2.	Pipes	17

4.6.3.	Bends	17

4.6.4.	Reducers and Branches	17

4.6.5.	Fabricated Covers	18

4.6.6.	Piping Supports	18

4.6.7.	Thermocouples	18

4.6.8.	Insulation Supports	18

4.6.9.	Security	18

4.6.10.	Cracks, Void, Breaks and etc.	18

4.6.11.	Storage	18

4.6.12.	Finishes and Appearance Cladding	18

4.6.13.	Table of Insulation Thickness	20

4.6.14.	Technical Specification of Removable Thermal Insulation Blanket	27

4.6.15.	Standard Drawings	28

# 1.	PRELIMINARIES

## 1.1	Introduction

The preliminary items, included hereunder, apply to the whole of the works contained in this Specification and the rates and / or amounts inserted by the Contractor in Schedule of Rates shall be deemed to apply to the whole of the works carried out under this Contract including all variations to the Contract.

The Contractor shall be deemed to have allowed in his tender for all costs in respect of all items described in this Specification.

In the absence of any sum against any preliminary item or items in the Schedule of Rates, any monetary cost attributable thereto shall be deemed to be included in the unit rates for the work.

Any price entered in the preliminary item or items in the Schedule of Rates shall be at the risk of the Contractor and no adjustment will be made at the settlement of accounts.

The documents forming the Contract are to be taken as mutually explanatory and the tendered sum shall be deemed to cover the complete requirement of the Conditions of Contract, Appendix to Conditions of Contract, Specification, Schedule of Rates and Drawings.

## 1.2	Scope of the Works

The scope of works to be performed is the one defined on Appendix 1.

## 1.3	Description of the Works

The descriptions of the Scope of the Works in this Specification must not be considered as being complete.

The Tenderer shall have experience for construction of industrial equipment and pipeline thermal insulation engineering during 2020-2024. If participating as  Consortium / Joint-Venture (JV), at least one Consortium / Joint-Venture (JV) member must have the related experience.

The tenderers must provide the Curriculum Vitae (CV) of the key members assigned for the project, Organization Chart for this project, etc. (instructions to tenderers document). The information submitted shall be able to prove that the Project Team has the Managerial Ability for this type of Project.

The Tenderer is deemed to have read this Specification, the Schedule of Rates and other related documents, visited the site and request to CEM all the information considered necessary to be fully aware of the full extent of the works.

The work, as specified with service configuration, shall be carried out strictly in the specified period of time, and according to the CEM Engineer’s instruction, in order not to affect normal operation of the Power Station.

According to CEM’s work instruction, the risk assessment – Job Hazard Analysis is required to conduct. The Contractor must submit the working schedule together with JHA of each individual work and must be agreed with the Engineer prior to execution.

CEM Engineer, from time to time, has the right to terminate any work in proceeding, if the Contractor’s performance cannot fulfill the conditions of the Contract or is not satisfactory for the CEM Engineer. No liability or claim shall be accepted under such circumstances.

## 1.4.	Site Inspection

### 1.4.1.	Location

The site of the works is mainly at CEM – Power Stations, and the Contractor may be required to carry out the same nature of work on CEM property at other locations.

### 1.4.2.	Site Visit

It is compulsory for the tenderer to visit the site of works and make themselves thoroughly acquainted with the location of where the project will be deployed. Accessibility, workspace conditions, nature of equipment and installations to be protected and any other conditions which may affect their tender. Tenderer who refuses or does not attend the site visit will be deemed disqualified. A site visit certificate will be issued to all attended tenderers who are required to submit the certificates in their tender document.

No claim for extra payment or extension of the working period will be allowed on the grounds of ignorance of the conditions under which the work is to be carried out.

The Contractor shall accept the site as found on the date for possession.

## 1.5.	Safety, Health and Environmental Precautions

It is mandatory for the contractor’s employees to receive the induction training conducted by CEM before starting the tender proposal.

The Contractor shall submit related JHA (Job Hazard Analysis) of the works to CEM for approval before the works.

The contractor shall not smoke in CEM premises as CEM is a smoke free workplace. Smoking is only allowed at designated smoking area.

The contractor shall perform the works in a manner of minimizing the potential impacts to the environment complying with ISO14001 and legal requirements.

The Contractor shall be responsible for the safety and health of all persons engaged in the execution of the works and shall take such safety and health precautions as are generally accepted as good practice.

A Safety, Health and Environment Officer (SHE Officer) must be assigned by the Contractor to be responsible for all the safety, health and environment related issues.

Before the works start, SHE Officer must ensure with CEM Engineer that all required solutions for waste management and any other environmental impacts exist. All waste generated must be reported to CEM Engineer.

SHE Officer and CEM Engineer shall agree, whenever necessary, to implement environmental impact mitigation measures, adequate condition and maintenance for safety and environmental protection equipment.

The Contractor must comply with Macao’s Legislation related with safety, health and environment. The works to be executed under this contract shall comply in all items with respect to the latest version of “Lei da segurança e saúde ocupacional na construção civil. – Lei n.º 2/2023” and Normas técnicas de segurança e saúde ocupacional na construção civil. – Regulamento Administrativo n.º 32/2023”.

The Contractor must follow the instructions provided by the CEM Engineer related with Site Regulations, Consignments and SHE related issues, in order to follow CEM’s Safety, Health, Environment and Quality Policy.

Considering the certain degree of hot work & heavy lifting will be involved, tenderer with certified / locally recognized firefighting, heavy lifting as well as DSAL Safety Officer training will be preferrable.

## 1.6.	  CEM Green Compliance Requirement

CEM has commitment to the environment.  All tenderers are required to comply with the requirements stated in “CEM Safety, Health, Environment and Quality Requirements & Responsibilities for Services Suppliers”.

Please refer to the Document “Green Compliance (CEM Green Compliance (for fill in)” of Tender document for the requirement. The tenderer is required to propose the offers to ensure alignment with the required items (if any) and elaborate on their Green Efforts or Green Actions in the proposal.

## 1.7. Protection of the Properties

The Contractor shall protect all existing public and CEM’s properties facilities, for which the Contractor shall be responsible and bear all cost incurred on making good and remedying any damage caused thereto.

## 1.8.	Materials and Workmanship

### 1.8.1	Compliance with Regulation

Materials, workmanship and the works as a whole must conform to or be of a higher standard than the minimum required by the bylaws of the Macau Government or any Statutory applicable to the works.

### 1.8.2	Proprietary Articles

The insertion of the name of any firm or proprietary article in the Specification is to be read as an indication of the class or quality of materials and workmanship required; goods or workmanship of equal quality may be obtained from any other firm, subject to the written approval of the CEM.

### 1.8.3.	Samples

The quality of materials and articles supplied for any purpose is to be approved prior to their use in the works. Wherever practicable, samples are to be submitted for approval before bulk supplies are delivered to the site. Samples, and any packing for it, are to be provided free of charge by the Contractor.

The Contractor shall submit or provide for approval all necessary samples before proceeding with the work.

Should any material or article be rejected, it shall be removed from the site at the Contractor’s expense.

Approved samples shall be kept on site to serve as a standard for all subsequent works.

### 1.8.4.	Safe Custody of Materials

The Contractor shall be responsible for the safe custody of all materials delivered to the site. The Contractor will be required to reinstate at the Contractor’s expense any such materials that may be lost or stolen.

The Contractor will also be required to reinstate at the Contractor’s expense any material or article damaged by careless handling or storage or inferior workmanship by his workmen, either in the original fixing or in the subsequent taking down and re-fixing thereof.

### 1.8.5.	Loading and Unloading of Materials

The Contractor shall take every care in the loading and off-loading of materials for the work and ensure that the street, roads and footpaths are not obstructed or the traffic impeded.

## 1.9.	Program and Reports

Once CEM awards the order to the Contractor, the work should be started immediately. If the work cannot be started due to unforeseen reasons or other problems, the Contractor should report immediately to CEM Engineer for further instruction.

As soon as the work is finished, the Contractor must submit the detail of report within three working days, which includes the information about quantities of material used, length/area of material, and duration of work etc., Beside this, the Contractor should provide additional information such as photos, drawings, and documents whenever the CEM Engineer is necessary.

## 1.10.	Temporary Works

### 1.10.1	Plant, Tools, Etc. and Scaffolding

The Contractor shall provide and maintain in good working conditions all the equipment, plant, tools, implements, ladders, tarpaulins and the like necessary for the proper and timely execution and protection of the works.

The Contractor shall provide sufficient reserve plant of all kinds to ensure that the work is not interrupted by breakdown of plant.

The Contractor shall erect and maintain suitable and safe ladders and gangways for CEM. The Site Engineer and Clerk of Works, and the representative of CEM, shall thoroughly inspect any portion of the works, with complete safety.

The Contractor shall design to the satisfaction of CEM, erect, alter, if necessary, and maintain all temporary props and supports to protection platforms, working platforms and especially to supporting existing equipment specified to remain in place throughout the work.

### 1.10.2.	Contractor’s Storage Sheds, Workshops and Offices

The Contractor shall provide for his own use all necessary workshops, mess rooms, offices and sheds of suitable construction for the storage of materials, maintain them in good order to the satisfaction of CEM, remove on completion of the Works and make the sites good.

All materials on the site shall be stored in a neat and orderly manner and to the satisfaction of CEM.

### 1.10.3.	Water, Electrical Power and Compressed Air for the Works

CEM can provide the on-site usage of water, electrical power and compressed air needed for this contract from the existing source of supply. The conditions are the following:

      - Water: tap water.

- Electricity: 400/230V AC, 3 phase, 50 Hz;

CEM will supply electrical power to a switchboard (supplied by the Contractor) equipped with a circuit breaker and earth leakage circuit protection.

- Compressed Air: service air, 7 bars max.

### 1.10.4.	Other Temporary Works

The Contractor shall provide all other necessary temporary works not specifically mentioned herein.

## 1.11.		Clearance of Site on Completion

After the completion of the works, the Contractor must clear away and remove from the site all Contractor’s equipment, surplus material, rubbish and temporary works of every kind, and leave the site and works clean and in a workmanlike condition to the satisfaction of CEM.

Disposal of all the Heavy Wastes of Big Size and/or of SHE Concerns from the Contracted Project/Work

All work executed on the Site shall be to the satisfaction of the Employer and in accordance with the safety requirements of the Employer.  The Contractor shall keep the Site, on which he erects or stores plant, safe and clean, removing all his wastes out of Coloane Power Station to the legal dumping sites as designated by Macau Government from the works as they accumulate.  On completion of the Works, the Site shall be left clean and tidy to the satisfaction of the Employer.  Any damage done to buildings, structures and plant or property belonging to the Employer shall be made good at the Contractor’s expense.

The Contractor shall submit a waste material disposal plan for approval, in order to ensure that the waste materials have been disposed in accordance with the CEM and Macau environmental regulations.

## 1.12.		Penalty

### 1.12.1.	Due to delays on the works

If the Contractor, due to his own fault, fails to comply with the time for completion in accordance with the time frame defined by CEM to complete the whole or part of the works and cause any consequence unavailability of the systems, then the Contractor shall pay to CEM, at the rate of 5% of the price of the relevant order per day of delay on the phase of work to be performed under this contract, up to a maximum of 20% of the price of the relevant order. CEM may, without prejudice to any other method of recovery, deduct the amount of such damages from any monies due to or become due to the Contractor. The payment or deduction of such damages shall not relieve the Contractor from his obligation to complete the works, or from any other of his obligations and liabilities under this Contract.

### 1.12.2.	Due to non compliance of CEM’s Safety and Environment requirements

If the contractor fails to comply with the Safety and Environmental CEM regulations, CEM will apply penalties to the Contractor, for details please refer to "SHE non-Compliance of Contracts Managed by CEM" the latest Version

## 1.13.		Guarantee

After the Contractor has completed his obligations and liabilities under each work, the Contractor still has full responsibility to correct any defect and to repair any damage in 12 (twelve) months period.

## 1.14.		Price

Price with conditions stated above should be listed according to Schedule of Rates. CEM takes no responsibility and does not pay for excess works and materials.

## 1.15.   General Remarks for this Specific Project

All the removed non-metal materials should be properly disposed by the Contractor in accordance with the related Macau Government Law.

All the removed metals are the properties of CEM, and they should be transported to the CEM scrap yard by confirmation of CEM Engineer.

Estimate and report the quantity (in Kg or Ton) of all the removed waste materials to the CEM Engineer in accordance with the following category:

Insulation materials.

Metallic materials.

Others.

Clean the site after the works.

# 2.	SCHEDULE OF RATES

In the Schedule of Rates, the following points should be considered:

- Requirements stated in the Technical Specification.

- Prices should be quoted on unit price basis.

Please fill in the document “190-25 Schedule of Rates” to provide your quotation.

Proposed prices are to be quoted, denominated and paid in the following currency:

- Macau Patacas (MOP)

The Price shall include all expenses related with the provision of the services on-site, at CEM in Macau, including lodging and travel, and TAX, when applicable.

The Price shall remain fixed and not subject to exchange rates variations or rise and fall provisions for the duration of the contract.

# 3.	CONTRACT EXECUTION

## 3.1.		Description of the Works

The description of the works is on Appendix 1.

## 3.2		Time for Completion of the Work

For each work awarded by the CEM should be carried out under the CEM Engineer specification requirement and instruction to complete the work.

## 3.3.		Works Procedure

### 3.3.1.	Preparation

The Contractor is requested to visit the site of the work for each order, to collect all the necessary information to perform work in accordance with this contract.

The Contractor shall prepare all necessary materials, tools and finish the preparation works in advance, to start the works in accordance with the schedule that agreed with CEM.

In case the work is necessary to erect scaffoldings, the Contractor should inform the CEM Engineer in advance, in order for him/her to prepare the necessary arrangement before processing the work.

CEM will allow the Contractor to have access to all existing technical documentation necessary to perform the works; all the technical documentation supplied to the Contractor remains CEM property; the Contractor is not allowed to disclose to any third party any copy of these documents without previous written permit from CEM.

The Contractor should prepare the risk assessment – Job Hazard Analysis for each work to be performed. The JHA must be submitted to CEM and obtained CEM’s approval before starting the work. The Contractor also has to fill in the relevant forms stated in Articles no.44 & 45 of Regulamento Administrativo n.º 32/2023 “Normas técnicas de segurança e saúde ocupacional na construção civil” and hand over all the relevant forms to CEM.

### 3.3.2.	Execution

For each work to be performed the Contractor shall receive a process with the identification of the equipment and work to be performed; the Contractor shall only start the works after receiving the Work Permit from the CEM Engineer. Any action is strictly forbidden without the Work Permit, and no delay is allowed.

The Contractor shall inform the CEM Engineer for inspection after the works are finished and hand over the Work Permit to him for de-consign the system.

The coordination of Contractor’s activities with CEM or other Contractors activities is of CEM responsibility.

### 3.3.3.	Other Contractor Responsibility

The Contractor is responsible to supply all the materials and products necessary to perform the works: tools, cleaning products and so on.

The contractor is responsible to supply legal human resource to complete the works deference in the specification.

The Tenderers are deemed to have read carefully the Specification, Schedule of Rates, Drawings, and other documents and in particular to have visited the Site to be fully aware of the full extent of the Works.

# 4.	APPENDIX 1

## 4.1.	Scope of works

The works include, but are not necessary limited to:

- Remove the damaged insulation and cladding from the piping or equipment indicated by CEM.

- Install new insulation and cladding for the piping or equipment indicated by CEM.

- Repair the insulation and cladding for the piping or equipment indicated by CEM.

- Erect scaffolding(s) for the above mentioned works (approval from CEM in advance is required)

## 4.2.	Insulation Material

The insulation of piping shall be designed, manufactured, inspected and tested in-accordance with but not limited to, the following Codes and Standards, including all addenda, in effect at the time of execution of contract.

a)	BS 5970: Code of Practice for Thermal Insulation of Pipework, Ductwork, associated Equipment and other Industrial Installations in the temperature Range of –100°C to +870°C).

b)	BS 3958: Specification for Thermal Insulating materials or equivalent standards.

For piping or equipment, insulation materials shall be magnesia, calcium silicate or mineral wool.

For piping or equipment insulation material shall conform to the requirements of physical properties as shown on the table 1.

Pre-formed materials shall be used for the insulation of pipe work or equipment but where the pipe size is too large for this to be practicable, suitable mats shall be used.

All insulation materials shall be vermin proof, non-hygroscopic, free of sulphur, chemically inert when both wet and dry, and fire resistant. Under no circumstances shall asbestos or asbestos-containing materials be used.

All insulation external to buildings shall be weather and waterproof.

Tenderer is requested to provide the MSDS, technical spec, brands of insulation that will be used for this tender.

| Type | Physical Forms |  |  |
| --- | --- | --- | --- |
|  | Pre-formed |  | Wired Mattresses |
|  | Calcium Silicate | Mineral Fibre Pipe Section |  |
| Material | BS 3958 |  |  |
| Applicable Size (Bare) | DN 350 & Smaller |  | DN 400 & Larger |
| Max. Operating Temperature | 800ºC | 650ºC | 850ºC |
| Density (Kg/cm3) | 190 to 260 | 100 to 150 | 80 to 150 |
| Thermal Conductivity | 0.061W/mK at mean temperature of 100°C | 0.052W/mK at mean temperature of 100°C | 0.050W/mK at mean temperature of 100°C |

Table 1

## 4.3.	Metal Cladding Material

Metal cladding shall be of aluminum.

Metal cladding shall be of thickness not less than those requirements:

| Cladding Thickness | Outer Insulation Diameter |
| --- | --- |
| 0.7 mm | Less than 150 mm |
| 0.9 mm | 150 mm to 450 mm |
| 1.2 mm | More than 450 mm |

* Aluminum cladding for equipment may require using pre-formed G.I. corrugated sheet.

Flanged valve and pipe flange insulation shall be enclosed by aluminum boxes. Those boxes shall be in two halves and fasten with quick release toggles to facilitate removal for inspection or maintenance without disturbing the insulation or sheathing on adjacent piping.

Other than the insulation materials and cladding (jacket), the awarded contractor must provide the necessary equipment & consumables for the fabrication of the requested industrial standard insulation e.g. clamp, binding wire, sheet-metal screw or rivet, roll-bending machine, sewing machine etc.

## 4.4.	Security Material

- Wire

The insulation materials shall be secured to pipe work by means of circumferential tie wire (diameter: 1.0mm to 1.6mm) at not greater than 500 mm spacing.

The material of wire shall be corrosion resistance and must be stainless steel.

- Self Tapping Screw

Self-tapping screw shall be M4x16mm length.

## 4.5.	Removal of Existing Insulation and Cladding

- Obtain the approval of CEM before commencing the works.

- Remove the obstacle facilities and keep all parts for relocation.

- The removed insulation materials must be packed, labeled and kept in a place that defined by CEM.

- Unless otherwise specified, materials arising from the demolition shall be kept inside the power station in a place to be instructed by CEM.

## 4.6.	Installation Specification

### 4.6.1.	General

During the application of heat insulation the Contractor shall protect adjacent facilities from damage. The Contract shall make good any damage at his own expense.

The insulation shall general be installed in accordance with the recommendation of BS 5970.

Piping shall be clean, dry and free from grease, dirt, loose or scale before application of insulation materials.

### 4.6.2.	Pipes

Sectional, tri-sectional and quad-segmental pipe insulation shall be applied on the straight pipe using staggered joint construction for single layer application and staggered and broken joint construction for multiple application as in clause 4.6.15. Figure 1 and 2.

Each section should be held by means of the circumferential wires at not greater than 500mm spacing. Over-tightening of wire should be avoided to prevent cracking of rigid material.

### 4.6.3.	Bends

Insulation of pipe bends shall be fabricated using miter-type construction as shown in clause 4.6.15. Figure 4.

Where multiple layer construction is required, each layer shall be fabricated and installed separately.

### 4.6.4.	Reducers and Branches

Reducers and Branches shall be installed as shown in Clause 4.6.15. Figure 5 and 6.

### 4.6.5.	Fabricated Covers

Where flanges and flanged valves are to be insulated the pipe work insulation shall be terminated short of the flanges to enable easy withdrawal of the flange bolts without damage to the insulation.

### 4.6.6.	Piping Supports

Piping supports shall be insulated as shown in Clause 4.6.15. Figure 3.

### 4.6.7.	Thermocouples

Thermocouple pocket boxes, pressure tapings shall be fitted with removable boxes or sections.

### 4.6.8.	Insulation Supports

On vertical or near vertical piping all insulation shall be supported in position by means of metal rings, part rings, studs or cleats at interval not greater than 3.6m and above each expansion break in the insulation.

The insulation supports should and penetrate the insulation more than is absolutely necessary for reliable support purposes.

On flat or large curved surfaces, the insulation material shall be supported by cleats or similar attachment welded or screwed to the surface being insulated. The average spacing of the cleats shall be:

-	For vertical surfaces			450mm

-	For upward facing surfaces		600mm

-	For overhanging and downward	300mm

### 4.6.9.	Security

The insulation materials shall be secured to pipe work by means of circumferential tie wires at not greater than 500mm spacing.

### 4.6.10.	Cracks, Void, Breaks and etc.

Cracks, voids, break or improperly fitted insulation shall not be allowed, and where present, insulation shall be refitted or replaced.

### 4.6.11.	Storage

When storing the heat insulation materials, be sufficiently careful with moisture, and be sure to use completely dried ones.

Also pay full attention to rain water, etc. even while the work is in progress.

### 4.6.12.	Finishes and Appearance Cladding

Metal cladding shall be provided to give a neat, smooth external finish and to protect the insulation of all pipe work.

Where insulation is in an outdoor application special attention shall be paid to the provision of weather-resistant finished and finished shall, as a minimum, comply with the recommendations of BS 5970.

The cladding shall be arranged in conveniently sized section and shall be shaped to suitably stiffen the sheets, allow for thermal expansion and to give a good appearance. Suitable framing shall be provided to which the sheeting shall be secured where necessary for its satisfactory support.

The arrangement of metal cladding shall be such as to minimize electrolytic corrosion, in the light of the corrosion risks on the site and in the position of the particular parts of the metal cladding. Unless otherwise agreed by purchaser, galvanized mild-steel cladding shall be secured with cadmium-plated, galvanized mild-steel or austenitic stainless-steel attachments; and aluminium sheets secured with aluminium or austenitic stainless-steel attachment.

Insulation finishing shall, where appropriate, include arrangements allow the escape of moisture trapped within cladding or other finishing. The cladding shall be watertight, self-draining and arranged at all inspection ports, doorways, etc. so that small sections can be easily detached for maintenance purposes.

All finished material shall incorporate provision for differential thermal expansion between the finish and the insulated surface. Where slots are cut to permit expansion, the ingress of dust or dirt is to be prevented by the use of straps or masking pieces to cover the slots. All joints for metallic jackets, to ensure prefect waterproof effect, should be overlapped 50mm wide in longitudinal joints and overlapped 50mm wide in circumferential direction as shown in Clause 4.6.15. Figure 1&2.

The joints of horizontal piping in longitudinal direction should be provided usually at a position of about 45° from the top, and for the vertical piping, the overlapped parts in circumferential direction should be all be turned downward for water shed. For the metallic jacketing on the vertical piping, the joints should be folded to partially to prevent the metallic jacket from sliding down from above.

### 4.6.13.	Table of Insulation Thickness

Insulation thickness shall be selected on insulation thickness table as shown in the table 2 - 7.

Table 2: 	Thermal Insulation Thickness

(Calcium Silicate)

Table 3: 	Thermal Insulation Thickness

(Mineral Fiber – Pipe Sections)

Table 4: 	Thermal Insulation Thickness

(Mineral Fiber – Mattresses)

Table 5:	Personnel protection Insulation Thickness

(Calcium Silicate)

Table 6: 	Personnel protection Insulation Thickness

(Mineral Fiber – Pipe Sections)

Table 7: 	Personnel protection Insulation Thickness

(Mineral Fiber – Mattresses)

The insulation thickness that specified in the tables is for reference only. The Contractor must consider the density of the insulation material that to be used and put the necessary thickness in order to achieve the required conditions:

| For Thermal Insulation Purpose | For Personal Protection Purpose |
| --- | --- |
| Condition: - Still Air Temperature : 32°C - Surface Temperature : 55ºC or below | Condition: - Still Air Temperature : 30°C - Surface Temperature : 35ºC or below |
| Two layers of insulation shall be used where the insulation thickness is not less than 50mm |  |

Table 2. Thermal Insulation Thickness ( Calcium Silicate )

Thickness : mm(inch)

| Temp (°C) Size | 150 & below | 151-200 | 201-250 | 251-300 | 301-350 | 351-400 | 401-450 | 451-500 | 501-550 | 551-600 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 15 | 25(1) | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 100(4) |
| 20 | 25(1) | 50(2) | 50(2) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 100(4) |
| 25 | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 100(4) | 100(4) |
| 50 | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 100(4) | 125(5) |
| 65 | 25(1) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) | 125(5) |
| 80 | 25(1) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) | 125(5) |
| 100 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) |
| 150 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) |
| 200 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) | 150(6) |
| 250 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) | 175(7) |
| 300 | 25(1) | 50(2) | 100(4) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 150(6) | 175(7) |
| 350 | 25(1) | 50(2) | 100(4) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 150(6) | 175(7) |
| 400 | 25(1) | 50(2) | 100(4) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) | 150(6) | 175(7) |
| 450 | 25(1) | 50(2) | 100(4) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) | 150(6) | 175(7) |
| 500 | 25(1) | 50(2) | 100(4) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) | 175(7) | 175(7) |
| 550 | 25(1) | 50(2) | 100(4) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) | 175(7) | 175(7) |
| 600 | 25(1) | 50(2) | 100(4) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) | 175(7) | 175(7) |
| Note: - Condition 1) Still Air Temperature : 32 °C 2) Surface Temperature : 55 °C or below - Two layers of insulation shall be used where the insulation thickness is not less than 50mm. |  |  |  |  |  |  |  |  |  |  |

Table 3. Thermal Insulation Thickness (Mineral Fibre – Pipe Sections)

Thickness : mm(inch)

| Temp (°C) Size | 150 & below | 151-200 | 201-250 | 251-300 | 301-350 | 351-400 | 401-450 | 451-500 | 501-550 | 551-600 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 15 | 25(1) | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) |
| 20 | 25(1) | 25(1) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) |
| 25 | 25(1) | 25(1) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) |
| 50 | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) |
| 65 | 25(1) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) |
| 80 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) | 150(6) | 150(6) |
| 100 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) | 175(7) |
| 150 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 150(6) | 175(7) |
| 200 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) |
| 250 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) |
| 300 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 125(5) | 125(5) | 150(6) | 175(7) | 200(8) |
| 350 | 25(1) | 50(2) | 50(2) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) | 175(7) | 225(9) |
| 400 | 25(1) | 50(2) | 50(2) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) | 225(9) |
| 450 | 25(1) | 50(2) | 50(2) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) | 225(9) |
| 500 | 25(1) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) | 225(9) |
| 550 | 25(1) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) | 225(9) |
| 600 | 25(1) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) | 225(9) |
| Note: - Condition 1) Still Air Temperature : 32 °C 2) Surface Temperature : 55 °C or below - Two layers of insulation shall be used where the insulation thickness is not less than 50mm. |  |  |  |  |  |  |  |  |  |  |

Table 4. Thermal Insulation Thickness (Mineral Fibre - Mattresses)

Thickness : mm(inch)

| Temp (°C) Size | 150 & below | 151-200 | 201-250 | 251-300 | 301-350 | 351-400 | 401-450 | 451-500 | 501-550 | 551-600 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 15 | 25(1) | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) |
| 20 | 25(1) | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) |
| 25 | 25(1) | 25(1) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) |
| 50 | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) |
| 65 | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) |
| 80 | 25(1) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 150(6) |
| 100 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) |
| 150 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 150(6) | 175(7) |
| 200 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) |
| 250 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) |
| 300 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) |
| 350 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 225(9) |
| 400 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 125(5) | 125(5) | 175(7) | 200(8) | 225(9) |
| 450 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) | 225(9) |
| 500 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) | 225(9) |
| 550 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) | 225(9) |
| 600 | 25(1) | 50(2) | 50(2) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) | 225(9) |
| Note: - Condition 1) Still Air Temperature : 32 °C 2) Surface Temperature : 55 °C or below - Two layers of insulation shall be used where the insulation thickness is not less than 50mm. |  |  |  |  |  |  |  |  |  |  |

Table 5. Personnel Protection Insulation Thickness ( Calcium Silicate )

Thickness : mm(inch)

| Temp (°C) Size | 150 & below | 151-200 | 201-250 | 251-300 | 301-350 | 351-400 | 401-450 | 451-500 | 501-550 | 551-600 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 15 | 25(1) | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 100(4) |
| 20 | 25(1) | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 100(4) |
| 25 | 25(1) | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 100(4) |
| 50 | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 100(4) | 125(5) |
| 65 | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 100(4) | 125(5) |
| 80 | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) | 125(5) |
| 100 | 25(1) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) | 125(5) |
| 150 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) |
| 200 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) |
| 250 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) | 150(6) | 150(6) |
| 300 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) | 150(6) |
| 350 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) | 150(6) |
| 400 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) | 175(7) |
| 450 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) | 175(7) |
| 500 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) | 175(7) |
| 550 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) | 175(7) |
| 600 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 150(6) | 175(7) |
| Note: - Condition 1) Still Air Temperature : 32 °C 2) Surface Temperature : 35 °C or below - Two layers of insulation shall be used where the insulation thickness is not less than 50mm. |  |  |  |  |  |  |  |  |  |  |

Table 6. Personnel Protection Insulation Thickness (Mineral Fibre-Pipe Sectons)

Thickness : mm(inch)

| Temp (°C) Size | 150 & below | 151-200 | 201-250 | 251-300 | 301-350 | 351-400 | 401-450 | 451-500 | 501-550 | 551-600 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 15 | 25(1) | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 125(5) |
| 20 | 25(1) | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) |
| 25 | 25(1) | 25(1) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) |
| 50 | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) | 150(6) |
| 65 | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) |
| 80 | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) |
| 100 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) | 150(6) | 150(6) |
| 150 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) | 175(7) |
| 200 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 150(6) | 175(7) |
| 250 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) |
| 300 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) |
| 350 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) |
| 400 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) |
| 450 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) |
| 500 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 125(5) | 125(5) | 150(6) | 175(7) | 200(8) |
| 550 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 125(5) | 125(5) | 150(6) | 175(7) | 225(9) |
| 600 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) | 225(9) |
| Note: - Condition 1) Still Air Temperature : 32 °C 2) Surface Temperature : 35 °C or below - Two layers of insulation shall be used where the insulation thickness is not less than 50mm. |  |  |  |  |  |  |  |  |  |  |

Table 7. Personnel Protection Insulation Thickness ( Mineral Fibre-Mattresses)

Thickness : mm(inch)

| Temp (°C) Size | 150 & below | 151-200 | 201-250 | 251-300 | 301-350 | 351-400 | 401-450 | 451-500 | 501-550 | 551-600 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 15 | 25(1) | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 75(3) | 100(4) | 100(4) | 125(5) |
| 20 | 25(1) | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) |
| 25 | 25(1) | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) |
| 50 | 25(1) | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) | 150(6) |
| 65 | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) | 150(6) |
| 80 | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 125(5) | 150(6) |
| 100 | 25(1) | 50(2) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 150(6) |
| 150 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) |
| 200 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 150(6) | 175(7) |
| 250 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) |
| 300 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) |
| 350 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) |
| 400 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) |
| 450 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 200(8) |
| 500 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 225(9) |
| 550 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 175(7) | 225(9) |
| 600 | 25(1) | 50(2) | 50(2) | 75(3) | 100(4) | 100(4) | 125(5) | 150(6) | 200(8) | 225(9) |
| Note: - Condition 1) Still Air Temperature : 32 °C 2) Surface Temperature : 35 °C or below - Two layers of insulation shall be used where the insulation thickness is not less than 50mm. |  |  |  |  |  |  |  |  |  |  |

### 4.6.14.	Technical Specification of Removable Thermal Insulation Blanket

Besides the cladding and insulation installation, removable thermal insulation blanket is an alternative choice for piping insulation. The tables below are the specification of the Fiberglass and Silicone Coated Fiberglass Cloth of the removable thermal insulation blanket used. For drawing details, Please refer to 4.6.15, Figure 7-Removable Thermal Insulation Blanket.

| Silicone Coated Fiberglass Cloth(Outer Layer) |  |  |  |
| --- | --- | --- | --- |
| 1 | Yarn (tex) | Warp: | EC9 66 1x3 |
|  |  | Weft: | EC9 66 1x3 |
| 2 | Cloth Thickness: |  | Min. 0.5 mm |
| 3 | Coat Style: |  | Double Silicone Rubber (200g) |
| 4 | Coat thickness: |  | 0.2 mm |
| 5 | Total thickness: |  | 0.7 mm |
| 6 | Total Weight: |  | Min. 800 g/m2 |
| 7 | Thread Count | Warp: | Min. 16 per cm |
|  |  | Weft: | Min. 15 per cm |
| 8 | Tensile Strength | Warp: | Min. 6000 N/5cm |
|  |  | Weft: | Min. 5000 N/5cm |
| 9 | Service Temperature: |  | Fiberglass: 550oC Silicone: 280oC |
| 10 | Temp. range of Sewing Thread: |  | 315oC - 760oC |
| 11 | Service Temp. of Mineral wool: (Needle Mat) |  | Min. 650oC |
| 12 | Sewing Method: |  | Hop "C" ring / Sewing Thread |

| Fiberglass Cloth (Inner Layer) |  |  |  |
| --- | --- | --- | --- |
| 1 | Yarn (tex) | Warp: | ET9 430 Tex |
|  |  | Weft: | ET9 430 Tex |
| 2 | Thickness: |  | Min. 0.75 mm |
| 3 | Weight: |  | Min. 580 g/m2 |
| 4 | Thread Count | Warp: | Min. 8 per cm |
|  |  | Weft: | Min. 5.7 per cm |
| 5 | Tensile Strength | Warp: | Min. 2700 N/5cm |
|  |  | Weft: | Min. 1800 N/5cm |
| 6 | L.O.I %: |  | <0.5% |
| 7 | Service Temperature: |  | 550oC |
| 8 | Temp. range of Sewing Thread: |  | 315oC - 760oC |
| 9 | Service Temp. of Mineral wool: (Needle Mat) |  | Min. 650oC |
| 10 | Sewing Method: |  | Hop "C" ring / Sewing Thread |

### 4.6.15.	Standard Drawings

Figure 1:	Single Layer Insulation for Horizontal pipe

Figure 2 : Multiple Layer Insulation for Horizontal pipe

Figure 3:	Insulation Details for Pipe Supports and Shoes

Figure 4:	Insulation Details for Pipe Bends and Elbows

Figure 5:	Insulation Details for Reducers

Figure 6:	Insulation Details for Branches

Figure 7:	Removable Thermal Insulation Blanket (Inner & Outer Layers)